## shoebox_ep_infil_
Date/Time | EP Input Infiltration Air Change Rate [ach] | EP Input Infiltration Volume Flow Rate [m3/s] | Environment:Site Outdoor Air Barometric Pressure [Pa] | Site Outdoor Air Drybulb Temperature [C] | Zone Air Temperature [C] | Infiltration Current Density Volume Flow Rate [m3/s] | Infiltration Mass Flow Rate [kg/s] | EP Infiltration Air Change Rate [ach] | TF (Temp Factor) = (Tout+273.15 / Tzone+273.15) [-] | Adjusted Outdoor Air Pressure = Pout * (1 − (elev * 2.25E-5))^5.2559 [Pa] | Adjusted Outdoor Air Density = adj_Pout / (R * Tout) [kg/m3] | Adjusted Zone Air Density = adj_Pout / (R * Tzone) [kg/m3] | Derived Mass Flow Rate = (ACH0.4 * Vzone * adj_out_dens / 3600) [kg/s] | Derived Volume Flow Rate = (ACH0.4 * TF * Vz) / 3600 | Adjusted ACH = ACH0.4 * TF [ach] | Adjusted ACH = der_mass/adj_zone_dens * 3600 / Vz [ach] | Adjusted ACH = ACH0.4 * (adj_out_dens / adj_zone_dens) [ach] | NODE 1:System Node Specific Heat [J/kg-K](Hourly) | MODEL OUTDOOR AIR NODE:System Node Specific Heat [J/kg-K](Hourly) | Sensible Heat Loss Energy [J] | W = adj_Pout * (Vol_out - Vol_zone) [J] | Q = (mass * 3600 * Cp_out * (Tout-Tin)) [J] | Qerr
01/01 01:00:00 | 0.4 | 0.016667 | 99291.6667 | -7.825 | 15.6 | 0.018167 | 0.021684 | 0.436 | 1.0883 | 96948.1882 | 1.2729 | 1.1697 | 0.021215 | 0.018138 | 0.43532 | 0.43532 | 0.43532 | 1009.259 | 1007.589 | 1845420.282 | 145.4222 | 1842473.9914 | 2946.2906
01/01 02:00:00 | 0.4 | 0.016667 | 99558.3333 | -11.9083 | 15.6 | 0.01845 | 0.022095 | 0.4428 | 1.1053 | 97208.561 | 1.2963 | 1.1728 | 0.021605 | 0.018422 | 0.44212 | 0.44212 | 0.44212 | 1008.475 | 1006.701 | 2202781.7917 | 173.3423 | 2202779.2183 | 2.5734
01/01 03:00:00 | 0.4 | 0.016667 | 99541.6667 | -11.35 | 15.6 | 0.0184 | 0.022043 | 0.4416 | 1.1029 | 97192.2877 | 1.2933 | 1.1726 | 0.021555 | 0.018382 | 0.44118 | 0.44118 | 0.44118 | 1007.903 | 1006.797 | 2153147.0749 | 168.4584 | 2153133.958 | 13.117
01/01 04:00:00 | 0.4 | 0.016667 | 99500 | -11.1 | 15.6 | 0.018376 | 0.022012 | 0.44102 | 1.1019 | 97151.6044 | 1.2915 | 1.1721 | 0.021526 | 0.018365 | 0.44076 | 0.44076 | 0.44076 | 1007.549 | 1006.842 | 2130244.941 | 166.0662 | 2130244.4384 | 0.50255
01/01 05:00:00 | 0.4 | 0.016667 | 99500 | -10.8083 | 15.6 | 0.018351 | 0.021986 | 0.44043 | 1.1007 | 97151.6044 | 1.2901 | 1.1721 | 0.021502 | 0.018344 | 0.44027 | 0.44027 | 0.44027 | 1007.323 | 1006.895 | 2104653.233 | 163.6526 | 2104646.319 | 6.9141
01/01 06:00:00 | 0.4 | 0.016667 | 99500 | -10.6 | 15.6 | 0.018334 | 0.021968 | 0.44001 | 1.0998 | 97151.6044 | 1.2891 | 1.1721 | 0.021485 | 0.01833 | 0.43992 | 0.43992 | 0.43992 | 1007.192 | 1006.934 | 2086396.67 | 161.9763 | 2086396.8971 | 0.22714
01/01 07:00:00 | 0.4 | 0.016667 | 99500 | -10.6 | 15.6 | 0.018332 | 0.021967 | 0.43997 | 1.0998 | 97151.6044 | 1.2891 | 1.1721 | 0.021485 | 0.01833 | 0.43992 | 0.43992 | 0.43992 | 1007.131 | 1007.001 | 2086414.8275 | 161.7805 | 2086414.9446 | 0.11713
01/01 08:00:00 | 0.4 | 0.016667 | 99500 | -10.25 | 15.6 | 0.018306 | 0.021935 | 0.43934 | 1.0983 | 97151.6044 | 1.2874 | 1.1721 | 0.021456 | 0.018305 | 0.43933 | 0.43933 | 0.43933 | 1007.138 | 1007.119 | 2055843.4881 | 159.2394 | 2055834.4365 | 9.0516
01/01 09:00:00 | 0.4 | 0.016667 | 99500 | -9.3583 | 15.6 | 0.018243 | 0.02186 | 0.43784 | 1.0946 | 97151.6044 | 1.283 | 1.1721 | 0.021384 | 0.018244 | 0.43785 | 0.43785 | 0.43785 | 1007.177 | 1007.194 | 1978262.1172 | 153.1747 | 1978233.2694 | 28.8478
01/01 10:00:00 | 0.4 | 0.016667 | 99500 | -7.6167 | 15.6 | 0.018124 | 0.021716 | 0.43497 | 1.0874 | 97151.6044 | 1.2746 | 1.1721 | 0.021243 | 0.018124 | 0.43497 | 0.43497 | 0.43497 | 1007.222 | 1007.247 | 1828252.2491 | 141.5433 | 1828135.2986 | 116.9505
01/01 11:00:00 | 0.4 | 0.016667 | 99441.6667 | -5.7083 | 15.6 | 0.017991 | 0.021542 | 0.43177 | 1.0797 | 97094.6479 | 1.2648 | 1.1714 | 0.021079 | 0.017995 | 0.43187 | 0.43187 | 0.43187 | 1007.306 | 1007.565 | 1665064.2043 | 128.5485 | 1664986.5125 | 77.6919
01/01 12:00:00 | 0.4 | 0.016667 | 99341.6667 | -4.0083 | 15.6 | 0.017873 | 0.021375 | 0.42894 | 1.0729 | 96997.0081 | 1.2555 | 1.1703 | 0.020925 | 0.017881 | 0.42914 | 0.42914 | 0.42914 | 1007.52 | 1008.057 | 1521117.3639 | 116.9809 | 1521040.2616 | 77.1023
01/01 13:00:00 | 0.4 | 0.016667 | 99241.6667 | -2.6583 | 15.6 | 0.017782 | 0.02124 | 0.42677 | 1.0675 | 96899.3683 | 1.248 | 1.1691 | 0.0208 | 0.017792 | 0.427 | 0.427 | 0.427 | 1007.814 | 1008.448 | 1407934.5329 | 108.0717 | 1407899.5149 | 35.0179
01/01 14:00:00 | 0.4 | 0.016667 | 99200 | -1.5583 | 15.6 | 0.01771 | 0.02114 | 0.42505 | 1.0632 | 96858.685 | 1.2424 | 1.1686 | 0.020707 | 0.01772 | 0.42527 | 0.42527 | 0.42527 | 1008.118 | 1008.725 | 1317241.113 | 101.0917 | 1317214.3115 | 26.8015
01/01 15:00:00 | 0.4 | 0.016667 | 99200 | -1.1 | 15.6 | 0.017682 | 0.021101 | 0.42436 | 1.0614 | 96858.685 | 1.2403 | 1.1686 | 0.020672 | 0.01769 | 0.42455 | 0.42455 | 0.42455 | 1008.396 | 1008.936 | 1279901.5945 | 98.2994 | 1279901.9213 | 0.32685
01/01 16:00:00 | 0.4 | 0.016667 | 99200 | -1.1 | 15.6 | 0.017681 | 0.021096 | 0.42435 | 1.0614 | 96858.685 | 1.2403 | 1.1686 | 0.020672 | 0.01769 | 0.42455 | 0.42455 | 0.42455 | 1008.657 | 1009.209 | 1279946.7669 | 98.2816 | 1279947.1073 | 0.34043
01/01 17:00:00 | 0.4 | 0.016667 | 99200 | -1.1 | 15.6 | 0.017683 | 0.021093 | 0.42439 | 1.0614 | 96858.685 | 1.2403 | 1.1686 | 0.020672 | 0.01769 | 0.42455 | 0.42455 | 0.42455 | 1008.909 | 1009.345 | 1279969.3531 | 98.4511 | 1279969.0051 | 0.34793
01/01 18:00:00 | 0.4 | 0.016667 | 99200 | -1.45 | 15.6 | 0.017709 | 0.021121 | 0.42501 | 1.0628 | 96858.685 | 1.2419 | 1.1686 | 0.020699 | 0.017713 | 0.4251 | 0.4251 | 0.4251 | 1009.084 | 1009.327 | 1308484.0398 | 100.9449 | 1308476.2914 | 7.7484
01/01 19:00:00 | 0.4 | 0.016667 | 99200 | -1.9917 | 15.6 | 0.017746 | 0.021163 | 0.4259 | 1.0649 | 96858.685 | 1.2444 | 1.1686 | 0.02074 | 0.017748 | 0.42595 | 0.42595 | 0.42595 | 1009.176 | 1009.31 | 1352744.7589 | 104.5315 | 1352738.6637 | 6.0953
01/01 20:00:00 | 0.4 | 0.016667 | 99200 | -1.5583 | 15.6 | 0.017716 | 0.021127 | 0.4252 | 1.0632 | 96858.685 | 1.2424 | 1.1686 | 0.020707 | 0.01772 | 0.42527 | 0.42527 | 0.42527 | 1009.238 | 1009.444 | 1317363.6911 | 101.6848 | 1317335.8641 | 27.8271
01/01 21:00:00 | 0.4 | 0.016667 | 99141.6667 | -1.45 | 15.6 | 0.017708 | 0.021103 | 0.425 | 1.0628 | 96801.7285 | 1.2412 | 1.1679 | 0.020686 | 0.017713 | 0.4251 | 0.4251 | 0.4251 | 1009.343 | 1009.631 | 1307762.1539 | 100.818 | 1307757.2918 | 4.862
01/01 22:00:00 | 0.4 | 0.016667 | 99100 | -1.35 | 15.6 | 0.017702 | 0.021084 | 0.42485 | 1.0624 | 96761.0452 | 1.2402 | 1.1674 | 0.02067 | 0.017706 | 0.42494 | 0.42494 | 0.42494 | 1009.458 | 1009.722 | 1299086.6966 | 100.1804 | 1299077.9021 | 8.7945
01/01 23:00:00 | 0.4 | 0.016667 | 99041.6667 | -1.45 | 15.6 | 0.01771 | 0.02108 | 0.42504 | 1.0628 | 96704.0887 | 1.2399 | 1.1667 | 0.020666 | 0.017713 | 0.4251 | 0.4251 | 0.4251 | 1009.547 | 1009.717 | 1306457.3736 | 100.8924 | 1306453.4382 | 3.9354
01/01 24:00:00 | 0.4 | 0.016667 | 99000 | -1.7 | 15.6 | 0.01773 | 0.021095 | 0.42553 | 1.0637 | 96663.4054 | 1.2406 | 1.1662 | 0.020676 | 0.017729 | 0.42549 | 0.42549 | 0.42549 | 1009.57 | 1009.477 | 1326230.5346 | 102.8122 | 1326230.0328 | 0.50179
Elevation |  |  | 201 | m2
Input ACH |  |  | 0.4 | 1/hr
Gas Constant |  |  | 287.05 | J/Kg-K
Zone Volume |  |  | 150 | m3
kWh = J / (3600 * 1000)
https://unmethours.com/question/16841/how-is-site-standard-air-density-calculated-in-energyplus/

## shoebox_ep_infil_simple
01/01 Hour | EP_Input_ACH | Site Outdoor Air Drybulb Temperature [C] | Zone Air Temperature [C] | Infiltration Current Density Volume Flow Rate [m3/s] | EP_Output_ACH | TF (Temp Factor) = (Tout+273.15 / Tzone+273.15) [-] | Derived Volume Flow Rate = (ACH0.4 * Vz) / 3600) * (Tout+273.15 / Tzone+273.15) | EP_Input_ACH * (Tout+273.15 / Tzone+273.15)
1 | 0.4 | -7.825 | 15.6 | 0.018167 | 0.436 | 1.0883 | 0.018138 | 0.43532
2 | 0.4 | -11.9083 | 15.6 | 0.01845 | 0.4428 | 1.1053 | 0.018422 | 0.44212
3 | 0.4 | -11.35 | 15.6 | 0.0184 | 0.4416 | 1.1029 | 0.018382 | 0.44118
4 | 0.4 | -11.1 | 15.6 | 0.018376 | 0.44102 | 1.1019 | 0.018365 | 0.44076
5 | 0.4 | -10.8083 | 15.6 | 0.018351 | 0.44043 | 1.1007 | 0.018344 | 0.44027
6 | 0.4 | -10.6 | 15.6 | 0.018334 | 0.44001 | 1.0998 | 0.01833 | 0.43992
7 | 0.4 | -10.6 | 15.6 | 0.018332 | 0.43997 | 1.0998 | 0.01833 | 0.43992
8 | 0.4 | -10.25 | 15.6 | 0.018306 | 0.43934 | 1.0983 | 0.018305 | 0.43933
9 | 0.4 | -9.3583 | 15.6 | 0.018243 | 0.43784 | 1.0946 | 0.018244 | 0.43785
10 | 0.4 | -7.6167 | 15.6 | 0.018124 | 0.43497 | 1.0874 | 0.018124 | 0.43497
11 | 0.4 | -5.7083 | 15.6 | 0.017991 | 0.43177 | 1.0797 | 0.017995 | 0.43187
12 | 0.4 | -4.0083 | 15.6 | 0.017873 | 0.42894 | 1.0729 | 0.017881 | 0.42914
13 | 0.4 | -2.6583 | 15.6 | 0.017782 | 0.42677 | 1.0675 | 0.017792 | 0.427
14 | 0.4 | -1.5583 | 15.6 | 0.01771 | 0.42505 | 1.0632 | 0.01772 | 0.42527
15 | 0.4 | -1.1 | 15.6 | 0.017682 | 0.42436 | 1.0614 | 0.01769 | 0.42455
16 | 0.4 | -1.1 | 15.6 | 0.017681 | 0.42435 | 1.0614 | 0.01769 | 0.42455
17 | 0.4 | -1.1 | 15.6 | 0.017683 | 0.42439 | 1.0614 | 0.01769 | 0.42455
18 | 0.4 | -1.45 | 15.6 | 0.017709 | 0.42501 | 1.0628 | 0.017713 | 0.4251
19 | 0.4 | -1.9917 | 15.6 | 0.017746 | 0.4259 | 1.0649 | 0.017748 | 0.42595
20 | 0.4 | -1.5583 | 15.6 | 0.017716 | 0.4252 | 1.0632 | 0.01772 | 0.42527
21 | 0.4 | -1.45 | 15.6 | 0.017708 | 0.425 | 1.0628 | 0.017713 | 0.4251
22 | 0.4 | -1.35 | 15.6 | 0.017702 | 0.42485 | 1.0624 | 0.017706 | 0.42494
23 | 0.4 | -1.45 | 15.6 | 0.01771 | 0.42504 | 1.0628 | 0.017713 | 0.4251
24 | 0.4 | -1.7 | 15.6 | 0.01773 | 0.42553 | 1.0637 | 0.017729 | 0.42549
Zone Volume |  | 150 | m3
Reference |  | https://unmethours.com/question/16841/how-is-site-standard-air-density-calculated-in-energyplus/